## AI Model Overview
# | AI Model Name | Category Tag | What It Does | Why It Matters | Total Parameters
01 | Anomaly Detection | Sensor | Flags abnormal sensor readings with severity score, confidence level, and asset affected — in minutes. | Eliminates alarm fatigue — only real events escalate to operations teams. | 12
02 | Leak / Burst Classifier | Network | Determines leak probability and burst probability per DMA — enabling targeted field dispatch. | Converts guesswork into GPS-precise crew deployment — reducing response from days to hours. | 12
03 | Pump Health Model | Asset | Predicts failure risk 7/30/90 days ahead using power, vibration, current and runtime data. | Converts emergency breakdowns into planned maintenance — saving cost and preventing outages. | 17
04 | Water Quality Risk Model | Quality | Calculates risk score, propagation zone and probable cause hours before a compliance breach. | Proactive safety — stops contamination reaching citizens before regulators are informed. | 12
05 | Demand Forecasting Engine | Supply | Projects demand, tank levels and supply requirements 6–24 hours ahead per distribution zone. | Enables proactive supply scheduling — eliminates reactive shortfalls and supply inequity. | 12
06 | Root Cause Assistant | Ops | Delivers plain-English incident explanations with ranked recommended actions in real time. | Cuts fault diagnosis from hours to minutes — junior staff operate at expert engineer level. | 14
07 | NRW Attribution Engine | Revenue | Separates real losses from apparent losses — attributing variance to leaks, meter errors or theft. | Tells management where to act — not just how much is being lost. Investment becomes targeted. | 12
08 | Energy Optimisation AI | Cost | Recommends optimal pump schedules using off-peak tariff windows, demand curves and efficiency. | Reduces pumping cost automatically — the largest variable OpEx — without manual intervention. | 15

## Parameter Register
Sr No | AI Model | Tag | Asset / Source | Parameter Name | Unit | Sensor / Transmitter | Protocol | Sampling Rate | AI Feature Role | Notes
1 | Anomaly Detection | Sensor | Electromagnetic Flow Meter | Flow Rate (instantaneous) | m³/h | 4-20 mA / Modbus RTU | 1 sec | Primary anomaly signal | Sudden drop/spike = pipe burst or blockage
2 | Anomaly Detection | Sensor | Pressure Transmitter | Pressure (discharge) | bar | 4-20 mA / HART | 1 sec | Pressure deviation feature | High pressure = closed valve; Low = burst
3 | Anomaly Detection | Sensor | Pressure Transmitter | Pressure (suction) | bar | 4-20 mA / HART | 1 sec | Suction anomaly detection | Cavitation signature detection
4 | Anomaly Detection | Sensor | CT Sensor on Booster Pump | Motor Current (per phase) | A | Modbus RTU | 1 sec | Electrical load anomaly | Phase imbalance, overload signature
5 | Anomaly Detection | Sensor | PT on LT Panel | Motor Voltage (R-Y-B) | V | Modbus RTU | 1 sec | Voltage anomaly feature | Under/over voltage events
6 | Anomaly Detection | Sensor | Ultrasonic Level Transmitter | Water Level (UGR/Sump) | m | 4-20 mA / Modbus | 5 sec | Level deviation from baseline | Unexpected drop = leak upstream
7 | Anomaly Detection | Sensor | DI on Starter Panel | Pump Running Status | On/Off | Digital Input | 1 sec | Operational state context | Anomaly scoring conditioned on pump state
8 | Anomaly Detection | Sensor | Vibration Sensor on Booster Pump | Vibration (X/Y/Z axis) | mm/s | 4-20 mA / Modbus | 1 sec | Mechanical anomaly signature | Imbalance, cavitation, bearing fault
9 | Anomaly Detection | Sensor | PT100 on Motor | Motor Winding Temperature | °C | 4-20 mA | 5 sec | Thermal anomaly feature | Rising temp without load change = fault
10 | Anomaly Detection | Sensor | Energy Meter on LT Panel | Power Consumption | kW | Modbus RTU | 5 sec | Power-flow ratio deviation | High power + low flow = wear anomaly
11 | Anomaly Detection | Sensor | Relay Output on Starter | Fault / Trip Status | Enum | Digital Input | 1 sec | Event trigger for model retraining | Trip events labelled for supervised learning
12 | Anomaly Detection | Sensor | Bulk Water Meter | Bulk Water Meter Reading | m³ | Pulse / Modbus RTU | 1 min | Zone-level flow baseline | DMA zone consumption pattern baseline
13 | Leak / Burst Classifier | Network | Electromagnetic Flow Meter (Inlet) | Flow Rate — DMA Inlet | m³/h | 4-20 mA / Modbus RTU | 1 sec | Primary leak signal | Night minimum flow (NMF) is key leak indicator
14 | Leak / Burst Classifier | Network | Electromagnetic Flow Meter (Outlet) | Flow Rate — DMA Outlet | m³/h | 4-20 mA / Modbus RTU | 1 sec | Zone balance calculation | Inlet - Outlet = apparent losses
15 | Leak / Burst Classifier | Network | Pressure Transmitter | Pressure (zone inlet) | bar | 4-20 mA / HART | 1 sec | Pressure-leak correlation | Low pressure at inlet = burst likely
16 | Leak / Burst Classifier | Network | Pressure Transmitter | Pressure (zone mid-point) | bar | 4-20 mA / HART | 1 sec | Pressure gradient across DMA | Steep gradient = active burst
17 | Leak / Burst Classifier | Network | Pressure Transmitter | Pressure (zone outlet) | bar | 4-20 mA / HART | 1 sec | End-of-zone pressure confirmation | Loss of pressure = downstream burst
18 | Leak / Burst Classifier | Network | Flow Meter (02:00–04:00 window) | Night Minimum Flow (NMF) | m³/h | Modbus RTU (aggregated) | 1 min | Core NRW / leak index | NMF > threshold = background leakage
19 | Leak / Burst Classifier | Network | Bulk Water Meter | Bulk Water Meter (zone) | m³ | Pulse / Modbus RTU | 15 min | Cumulative zone balance | Billing meter vs DMA meter = apparent loss
20 | Leak / Burst Classifier | Network | Limit Switch / Actuator Feedback | Discharge Sluice Valve Status | Open/Closed | Modbus RTU / DI | 5 sec | Network topology context | Closed valve changes expected flow pattern
21 | Leak / Burst Classifier | Network | Limit Switch on NRV | NRV Status | Open/Closed | Digital Input | 5 sec | Reverse flow detection | Open NRV during low-pressure = backflow
22 | Leak / Burst Classifier | Network | Actuator Position Feedback | Suction Sluice Valve Position | % | 4-20 mA / Modbus | 5 sec | Valve topology state | Partial closure distorts zone balance
23 | Leak / Burst Classifier | Network | Ultrasonic Level Transmitter | UGR Water Level | m | 4-20 mA / Modbus | 1 min | Supply-side context | Falling UGR level + constant pump hours = loss
24 | Leak / Burst Classifier | Network | Software Counter | Pump Run Hours (zone pumps) | hrs | Modbus RTU | 1 min | Supply volume cross-check | Hours × rated flow vs metered volume
25 | Pump Health Model | Asset | CT Sensor | Motor Current (per phase R-Y-B) | A | Modbus RTU | 1 sec | Load & imbalance feature | Phase imbalance >5% = winding fault risk
26 | Pump Health Model | Asset | PT / Energy Meter | Motor Voltage (R-Y-B) | V | Modbus RTU | 1 sec | Voltage stress feature | Voltage deviation = insulation stress
27 | Pump Health Model | Asset | Energy Meter on LT Panel | Power Factor | PF | Modbus RTU | 5 sec | Efficiency degradation indicator | Falling PF at constant load = wear
28 | Pump Health Model | Asset | Energy Meter | Active Power (kW) | kW | Modbus RTU | 5 sec | Power-flow ratio (specific energy) | kW/m³ rising = pump efficiency declining
29 | Pump Health Model | Asset | Electromagnetic Flow Meter | Flow Rate | m³/h | 4-20 mA / Modbus RTU | 1 sec | Duty point tracking | Flow drift from design curve = impeller wear
30 | Pump Health Model | Asset | Pressure Transmitter | Discharge Pressure | bar | 4-20 mA / HART | 1 sec | Head generation feature | Head drop at same flow = wear/impeller fault
31 | Pump Health Model | Asset | Pressure Transmitter | Suction Pressure | bar | 4-20 mA / HART | 1 sec | NPSH / cavitation risk | Low NPSH → cavitation → impeller erosion
32 | Pump Health Model | Asset | Vibration Sensor | Vibration (X-axis — radial) | mm/s | 4-20 mA / Modbus | 1 sec | Bearing & imbalance signature | ISO 10816 velocity bands for severity
33 | Pump Health Model | Asset | Vibration Sensor | Vibration (Y-axis — radial) | mm/s | 4-20 mA / Modbus | 1 sec | Misalignment signature | Y vs X ratio indicates misalignment
34 | Pump Health Model | Asset | Vibration Sensor | Vibration (Z-axis — axial) | mm/s | 4-20 mA / Modbus | 1 sec | Axial thrust fault | High axial = thrust bearing failure risk
35 | Pump Health Model | Asset | PT100 embedded in motor | Motor Winding Temperature | °C | 4-20 mA | 5 sec | Thermal health feature | Trending up without load change = insulation fail
36 | Pump Health Model | Asset | PT100 on bearing housing | Bearing Temperature (DE/NDE) | °C | 4-20 mA | 5 sec | Bearing wear indicator | ΔTemp >10°C from baseline = lubrication fail
37 | Pump Health Model | Asset | Software Counter | Run Hours (total lifetime) | hrs | Modbus RTU | 1 min | Remaining useful life estimate | Combined with starts count for lifecycle model
38 | Pump Health Model | Asset | Software Counter | Start Count | Count | Modbus RTU | Per event | Starting stress accumulation | Each start = stress cycle on windings/capacitor
39 | Pump Health Model | Asset | DI on Starter Panel | Starter Type / Transition Status | Enum | Digital Input | Per event | Soft start quality feature | Star-delta transition shock vs soft starter
40 | Pump Health Model | Asset | VFD Register | VFD Output Frequency (if fitted) | Hz | Modbus RTU | 1 sec | Speed-health correlation | Efficiency map vs current speed setpoint
41 | Pump Health Model | Asset | Relay + SCADA log | Fault / Trip History | Enum | Digital Input | Per event | Failure mode labelling | Ground truth for supervised failure model
42 | Water Quality Risk Model | Quality | Chlorine Analyser (online) | Residual Chlorine | mg/L | 4-20 mA / Modbus | 5 min | Primary quality indicator | < 0.2 mg/L triggers compliance alert
43 | Water Quality Risk Model | Quality | Turbidity Sensor (online) | Turbidity | NTU | 4-20 mA / Modbus | 5 min | Contamination ingress signal | Sudden spike = mains intrusion or soil entry
44 | Water Quality Risk Model | Quality | pH Probe (online) | pH Level | pH | 4-20 mA / Modbus | 5 min | Chemical balance indicator | pH < 6.5 or > 9.5 = treatment failure
45 | Water Quality Risk Model | Quality | Conductivity Sensor | Conductivity / TDS | µS/cm | 4-20 mA / Modbus | 5 min | Salinity / contamination proxy | Rising TDS = aquifer contamination risk
46 | Water Quality Risk Model | Quality | Temperature Sensor (inline) | Temperature (water) | °C | 4-20 mA | 5 min | Bacterial growth risk feature | >25°C promotes Legionella growth
47 | Water Quality Risk Model | Quality | Pressure Transmitter | Pressure (network zone) | bar | 4-20 mA / HART | 1 min | Intrusion risk — negative pressure | Transient negative pressure = contamination ingress
48 | Water Quality Risk Model | Quality | Electromagnetic Flow Meter | Flow Rate (zone) | m³/h | 4-20 mA / Modbus RTU | 1 min | Stagnation / retention time estimate | Low flow = long retention = chlorine decay
49 | Water Quality Risk Model | Quality | Ultrasonic Level Transmitter | Water Level (UGR / Service Res.) | m | 4-20 mA / Modbus | 5 min | Reservoir retention time | High level + low demand = stagnation risk
50 | Water Quality Risk Model | Quality | Limit Switch / Actuator | Valve Status (zone isolation) | Open/Closed | Modbus RTU / DI | 1 min | Network topology for propagation model | Closed valves define contamination boundary
51 | Water Quality Risk Model | Quality | DI on Starter | Pump Running Status | On/Off | Digital Input | 1 sec | Treatment dosing flow context | Pumping without dosing = residual collapse
52 | Water Quality Risk Model | Quality | Dosing Pump / Flow Controller | Chlorine Dose Rate | L/h | 4-20 mA / Modbus | 5 min | Treatment adequacy feature | Dose vs flow ratio = effective residual
53 | Water Quality Risk Model | Quality | Bulk Water Meter | Bulk Water Meter Reading | m³ | Pulse / Modbus RTU | 15 min | Consumption-decay correlation | Low consumption zones = high decay risk
54 | Demand Forecasting Engine | Supply | Bulk Water Meter | Bulk Water Meter (zone inlet) | m³ | Pulse / Modbus RTU | 15 min | Historical demand pattern (primary) | Zone-level 24h rolling consumption profile
55 | Demand Forecasting Engine | Supply | Electromagnetic Flow Meter | Flow Rate (instantaneous) | m³/h | 4-20 mA / Modbus RTU | 1 min | Real-time demand signal | Actual vs forecast deviation trigger
56 | Demand Forecasting Engine | Supply | Ultrasonic Level Transmitter | Water Level — UGR | m | 4-20 mA / Modbus | 5 min | Storage buffer state | Falling level = supply insufficient for demand
57 | Demand Forecasting Engine | Supply | Ultrasonic Level Transmitter | Water Level — Overhead Tank (OHT) | m | 4-20 mA / Modbus | 5 min | Distribution buffer state | OHT low = scheduled pump required
58 | Demand Forecasting Engine | Supply | DI on Starter Panel | Pump Run Status (all pumps) | On/Off | Digital Input | 1 sec | Current supply rate context | Which pumps are contributing to supply
59 | Demand Forecasting Engine | Supply | Electromagnetic Flow Meter | Pump Flow Rate (per pump) | m³/h | 4-20 mA / Modbus RTU | 1 min | Per-pump supply contribution | Used to allocate demand across pump schedule
60 | Demand Forecasting Engine | Supply | VFD Register | VFD Frequency (if fitted) | Hz | Modbus RTU | 1 sec | Variable speed flow control | Speed setpoint vs zone pressure/demand
61 | Demand Forecasting Engine | Supply | Pressure Transmitter | Pressure (zone) | bar | 4-20 mA / HART | 1 min | Demand-pressure relationship | Pressure-dependent demand modelling
62 | Demand Forecasting Engine | Supply | Actuator / Limit Switch | Discharge Sluice Valve Status | Open/Closed | Modbus RTU / DI | 1 min | Network availability state | Valve closed = zone isolated from supply
63 | Demand Forecasting Engine | Supply | DI on ATS Panel | ATS / Changeover Switch Status | Mains/DG | Digital Input | 1 sec | Power availability context | DG mode = limited pump capacity
64 | Demand Forecasting Engine | Supply | Energy Meter on LT Panel | Energy Consumption (kWh) | kWh | Modbus RTU | 15 min | Supply cost per m³ optimisation | Schedule shifts to off-peak tariff windows
65 | Demand Forecasting Engine | Supply | Software Counter | Run Hours (per pump) | hrs | Modbus RTU | 1 min | Available pump capacity | Exclude pumps near maintenance threshold
66 | Root Cause Assistant | Ops | Relay Output / DI on all panels | Fault / Trip Status (all assets) | Enum | Digital Input | Per event | Event trigger — root cause context | Trip event initiates root cause analysis
67 | Root Cause Assistant | Ops | CT Sensor | Motor Current (all 3 phases) | A | Modbus RTU | 1 sec | Phase fault pattern recognition | Single-phase loss, overload signature
68 | Root Cause Assistant | Ops | PT / Energy Meter | Voltage (R-Y-B phases) | V | Modbus RTU | 1 sec | Supply quality at time of fault | Voltage sag correlates with network fault
69 | Root Cause Assistant | Ops | Electromagnetic Flow Meter | Flow Rate at time of fault | m³/h | 4-20 mA / Modbus RTU | 1 sec | Hydraulic state context | No flow + running pump = valve closed or burst
70 | Root Cause Assistant | Ops | Pressure Transmitter | Pressure at time of fault | bar | 4-20 mA / HART | 1 sec | System state at fault moment | Pressure spike = waterhammer event
71 | Root Cause Assistant | Ops | Vibration Sensor | Vibration at time of fault | mm/s | 4-20 mA / Modbus | 1 sec | Mechanical fault signature | High vibration before trip = bearing/impeller
72 | Root Cause Assistant | Ops | PT100 | Bearing Temperature | °C | 4-20 mA | 5 sec | Thermal root cause evidence | Temperature pre-fault trend analysis
73 | Root Cause Assistant | Ops | PT100 in Motor | Winding Temperature | °C | 4-20 mA | 5 sec | Thermal overload root cause | Insulation breakdown pattern
74 | Root Cause Assistant | Ops | DI on Starter | Starter Status at fault | Enum | Digital Input | Per event | Starting mode context | Star-delta transition fail vs run fault
75 | Root Cause Assistant | Ops | Limit Switch / Actuator | Valve Positions at fault | Open/Closed | Modbus RTU / DI | Per event | Hydraulic topology at fault | Closed valve = root cause of no-flow trip
76 | Root Cause Assistant | Ops | Ultrasonic Level Transmitter | UGR/Sump Level at fault | m | 4-20 mA / Modbus | 5 sec | Supply-side fault context | Empty sump = dry run trip root cause
77 | Root Cause Assistant | Ops | DI on ATS | Power Supply Status (ATS/DG) | Mains/DG | Digital Input | Per event | Power root cause (grid vs DG fault) | Mains failure = ATS cause, not pump cause
78 | Root Cause Assistant | Ops | SCADA / PLC event log | Historical fault log | Log | Modbus TCP / SCADA DB | Continuous | Fault pattern matching | Similar past events ranked by similarity
79 | Root Cause Assistant | Ops | SCADA alarm log | Alarm sequence (pre-fault) | Log | SCADA DB | Continuous | Causal chain reconstruction | Alarm cascade sequence identifies root cause
80 | NRW Attribution Engine | Revenue | Bulk Water Meter (inlet) | Bulk Water Meter — Zone Inlet | m³ | Pulse / Modbus RTU | 15 min | System input volume | Primary NRW calculation input
81 | NRW Attribution Engine | Revenue | Bulk Water Meter (outlet) | Bulk Water Meter — Zone Outlet | m³ | Pulse / Modbus RTU | 15 min | Zone boundary metering | Inlet - Outlet = zone losses
82 | NRW Attribution Engine | Revenue | Inline Flow Meter (DMA) | Electromagnetic Flow Meter | m³/h | 4-20 mA / Modbus RTU | 1 min | Real-time loss rate | Flow imbalance per DMA = pinpoints loss zone
83 | NRW Attribution Engine | Revenue | Aggregated from flow meters | Night Minimum Flow (02-04h) | m³/h | SCADA aggregation | 1 min | Background real loss index | NMF - legitimate night use = real leakage
84 | NRW Attribution Engine | Revenue | Multiple Pressure Transmitters | Pressure (zone average) | bar | 4-20 mA / HART | 15 min | Pressure-leakage exponent (N1 model) | Higher pressure = exponentially more leakage
85 | NRW Attribution Engine | Revenue | AMR / Smart Meter | Consumer Meter Reading | m³ | AMR / Pulse / GPRS | 1 hr | Authorised consumption baseline | Billed volume vs metered zone input
86 | NRW Attribution Engine | Revenue | Actuator Position Feedback | Discharge Sluice Valve Position | % | Modbus RTU / 4-20 mA | 5 min | Zone topology — loss boundary | Valve state defines NRW accounting boundary
87 | NRW Attribution Engine | Revenue | Limit Switch | NRV Check Valve Status | Open/Closed | Digital Input | 5 min | Reverse flow / backflow losses | Faulty NRV = backflow = apparent losses
88 | NRW Attribution Engine | Revenue | Software Counter | Pump Run Hours | hrs | Modbus RTU | 1 min | Supply volume cross-check | Hours × rated flow vs bulk meter = meter error
89 | NRW Attribution Engine | Revenue | Ultrasonic Level Transmitter | Water Level — UGR | m | 4-20 mA / Modbus | 5 min | Storage volume change | ΔLevel × area = supply volume correction
90 | NRW Attribution Engine | Revenue | Limit Switch | Flushing Valve Status | Open/Closed | Digital Input | Per event | Operational loss tracking | Flushing volume subtracted from NRW calc
91 | NRW Attribution Engine | Revenue | DI | Solenoid Valve Status | On/Off | Digital Input | Per event | Controlled use vs unaccounted loss | Identify unauthorised operation events
92 | Energy Optimisation AI | Cost | Energy Meter on LT Panel | Active Power (kW) per pump | kW | Modbus RTU | 1 min | Real-time energy cost signal | Cost per m³ = kW / flow rate (specific energy)
93 | Energy Optimisation AI | Cost | Energy Meter / APFC Panel | Reactive Power (kVAR) | kVAR | Modbus RTU | 5 min | Power factor penalty cost | Low PF = kVAR charge from utility
94 | Energy Optimisation AI | Cost | Energy Meter | Energy Consumption (kWh) | kWh | Modbus RTU | 15 min | Tariff window billing tracking | Off-peak vs peak kWh comparison
95 | Energy Optimisation AI | Cost | APFC Panel / Energy Meter | Power Factor | PF | Modbus RTU | 5 min | Capacitor bank switching optimisation | Target PF > 0.95 to avoid utility penalty
96 | Energy Optimisation AI | Cost | Electromagnetic Flow Meter | Flow Rate (per pump) | m³/h | 4-20 mA / Modbus RTU | 1 min | Specific energy (kWh/m³) calculation | Pump efficiency curve operating point
97 | Energy Optimisation AI | Cost | Pressure Transmitter | Discharge Pressure | bar | 4-20 mA / HART | 1 min | System resistance curve point | Throttling losses = wasted energy
98 | Energy Optimisation AI | Cost | Pressure Transmitter | Suction Pressure | bar | 4-20 mA / HART | 1 min | Net head calculation | Differential head = energy per m³ pumped
99 | Energy Optimisation AI | Cost | VFD Register | VFD Frequency / Speed Setpoint | Hz | Modbus RTU | 1 sec | Speed optimisation signal | Affinity laws: speed² ∝ power → huge savings
100 | Energy Optimisation AI | Cost | Ultrasonic Level Transmitter | UGR Water Level | m | 4-20 mA / Modbus | 5 min | Storage buffer for off-peak scheduling | Fill UGR at off-peak; coast through peak
101 | Energy Optimisation AI | Cost | Ultrasonic Level Transmitter | OHT / Tank Level | m | 4-20 mA / Modbus | 5 min | Demand buffer state | High tank = delay next pump start
102 | Energy Optimisation AI | Cost | Software Counter | Pump Run Hours (lifetime) | hrs | Modbus RTU | 1 min | Schedule balances wear across pumps | Rotate duty/standby to equalise hours
103 | Energy Optimisation AI | Cost | DI on ATS | ATS Status (Mains vs DG) | Enum | Digital Input | 1 sec | Tariff mode — DG running cost context | DG fuel cost >> mains; avoid DG pumping
104 | Energy Optimisation AI | Cost | CT Sensor | Motor Current (all phases) | A | Modbus RTU | 1 sec | Motor efficiency point tracking | Current vs speed vs flow = efficiency map
105 | Energy Optimisation AI | Cost | DI on APFC Panel | Capacitor Bank Step Status | On/Off | Digital Input | 1 min | Reactive compensation adequacy | Optimise APFC switching to hold PF target
106 | Energy Optimisation AI | Cost | SCADA / PLC setpoint | Pump Start/Stop Schedule | Schedule | Modbus TCP | Per command | Schedule optimisation output | AI output drives pump start/stop commands

## 01 Anomaly Detection
01 ANOMALY DETECTION
WHAT: Flags abnormal sensor readings with severity score, confidence level, and asset affected — in minutes. |  |  |  |  | WHY IT MATTERS: Eliminates alarm fatigue — only real events escalate to operations teams.
Category: Sensor |  | Total Parameters: 12
# | Parameter Name | Source Asset | Unit | Sensor / Transmitter | Protocol | Sampling Rate | AI Feature Role | Notes / Alert Condition
1 | Flow Rate (instantaneous) | Electromagnetic Flow Meter | m³/h | 4-20 mA / Modbus RTU | 1 sec | Primary anomaly signal | Sudden drop/spike = pipe burst or blockage
2 | Pressure (discharge) | Pressure Transmitter | bar | 4-20 mA / HART | 1 sec | Pressure deviation feature | High pressure = closed valve; Low = burst
3 | Pressure (suction) | Pressure Transmitter | bar | 4-20 mA / HART | 1 sec | Suction anomaly detection | Cavitation signature detection
4 | Motor Current (per phase) | CT Sensor on Booster Pump | A | Modbus RTU | 1 sec | Electrical load anomaly | Phase imbalance, overload signature
5 | Motor Voltage (R-Y-B) | PT on LT Panel | V | Modbus RTU | 1 sec | Voltage anomaly feature | Under/over voltage events
6 | Water Level (UGR/Sump) | Ultrasonic Level Transmitter | m | 4-20 mA / Modbus | 5 sec | Level deviation from baseline | Unexpected drop = leak upstream
7 | Pump Running Status | DI on Starter Panel | On/Off | Digital Input | 1 sec | Operational state context | Anomaly scoring conditioned on pump state
8 | Vibration (X/Y/Z axis) | Vibration Sensor on Booster Pump | mm/s | 4-20 mA / Modbus | 1 sec | Mechanical anomaly signature | Imbalance, cavitation, bearing fault
9 | Motor Winding Temperature | PT100 on Motor | °C | 4-20 mA | 5 sec | Thermal anomaly feature | Rising temp without load change = fault
10 | Power Consumption | Energy Meter on LT Panel | kW | Modbus RTU | 5 sec | Power-flow ratio deviation | High power + low flow = wear anomaly
11 | Fault / Trip Status | Relay Output on Starter | Enum | Digital Input | 1 sec | Event trigger for model retraining | Trip events labelled for supervised learning
12 | Bulk Water Meter Reading | Bulk Water Meter | m³ | Pulse / Modbus RTU | 1 min | Zone-level flow baseline | DMA zone consumption pattern baseline

## 02 Leak - Burst Classifier
02 LEAK / BURST CLASSIFIER
WHAT: Determines leak probability and burst probability per DMA — enabling targeted field dispatch. |  |  |  |  | WHY IT MATTERS: Converts guesswork into GPS-precise crew deployment — reducing response from days to hours.
Category: Network |  | Total Parameters: 12
# | Parameter Name | Source Asset | Unit | Sensor / Transmitter | Protocol | Sampling Rate | AI Feature Role | Notes / Alert Condition
1 | Flow Rate — DMA Inlet | Electromagnetic Flow Meter (Inlet) | m³/h | 4-20 mA / Modbus RTU | 1 sec | Primary leak signal | Night minimum flow (NMF) is key leak indicator
2 | Flow Rate — DMA Outlet | Electromagnetic Flow Meter (Outlet) | m³/h | 4-20 mA / Modbus RTU | 1 sec | Zone balance calculation | Inlet - Outlet = apparent losses
3 | Pressure (zone inlet) | Pressure Transmitter | bar | 4-20 mA / HART | 1 sec | Pressure-leak correlation | Low pressure at inlet = burst likely
4 | Pressure (zone mid-point) | Pressure Transmitter | bar | 4-20 mA / HART | 1 sec | Pressure gradient across DMA | Steep gradient = active burst
5 | Pressure (zone outlet) | Pressure Transmitter | bar | 4-20 mA / HART | 1 sec | End-of-zone pressure confirmation | Loss of pressure = downstream burst
6 | Night Minimum Flow (NMF) | Flow Meter (02:00–04:00 window) | m³/h | Modbus RTU (aggregated) | 1 min | Core NRW / leak index | NMF > threshold = background leakage
7 | Bulk Water Meter (zone) | Bulk Water Meter | m³ | Pulse / Modbus RTU | 15 min | Cumulative zone balance | Billing meter vs DMA meter = apparent loss
8 | Discharge Sluice Valve Status | Limit Switch / Actuator Feedback | Open/Closed | Modbus RTU / DI | 5 sec | Network topology context | Closed valve changes expected flow pattern
9 | NRV Status | Limit Switch on NRV | Open/Closed | Digital Input | 5 sec | Reverse flow detection | Open NRV during low-pressure = backflow
10 | Suction Sluice Valve Position | Actuator Position Feedback | % | 4-20 mA / Modbus | 5 sec | Valve topology state | Partial closure distorts zone balance
11 | UGR Water Level | Ultrasonic Level Transmitter | m | 4-20 mA / Modbus | 1 min | Supply-side context | Falling UGR level + constant pump hours = loss
12 | Pump Run Hours (zone pumps) | Software Counter | hrs | Modbus RTU | 1 min | Supply volume cross-check | Hours × rated flow vs metered volume

## 03 Pump Health Model
03 PUMP HEALTH MODEL
WHAT: Predicts failure risk 7/30/90 days ahead using power, vibration, current and runtime data. |  |  |  |  | WHY IT MATTERS: Converts emergency breakdowns into planned maintenance — saving cost and preventing outages.
Category: Asset |  | Total Parameters: 17
# | Parameter Name | Source Asset | Unit | Sensor / Transmitter | Protocol | Sampling Rate | AI Feature Role | Notes / Alert Condition
1 | Motor Current (per phase R-Y-B) | CT Sensor | A | Modbus RTU | 1 sec | Load & imbalance feature | Phase imbalance >5% = winding fault risk
2 | Motor Voltage (R-Y-B) | PT / Energy Meter | V | Modbus RTU | 1 sec | Voltage stress feature | Voltage deviation = insulation stress
3 | Power Factor | Energy Meter on LT Panel | PF | Modbus RTU | 5 sec | Efficiency degradation indicator | Falling PF at constant load = wear
4 | Active Power (kW) | Energy Meter | kW | Modbus RTU | 5 sec | Power-flow ratio (specific energy) | kW/m³ rising = pump efficiency declining
5 | Flow Rate | Electromagnetic Flow Meter | m³/h | 4-20 mA / Modbus RTU | 1 sec | Duty point tracking | Flow drift from design curve = impeller wear
6 | Discharge Pressure | Pressure Transmitter | bar | 4-20 mA / HART | 1 sec | Head generation feature | Head drop at same flow = wear/impeller fault
7 | Suction Pressure | Pressure Transmitter | bar | 4-20 mA / HART | 1 sec | NPSH / cavitation risk | Low NPSH → cavitation → impeller erosion
8 | Vibration (X-axis — radial) | Vibration Sensor | mm/s | 4-20 mA / Modbus | 1 sec | Bearing & imbalance signature | ISO 10816 velocity bands for severity
9 | Vibration (Y-axis — radial) | Vibration Sensor | mm/s | 4-20 mA / Modbus | 1 sec | Misalignment signature | Y vs X ratio indicates misalignment
10 | Vibration (Z-axis — axial) | Vibration Sensor | mm/s | 4-20 mA / Modbus | 1 sec | Axial thrust fault | High axial = thrust bearing failure risk
11 | Motor Winding Temperature | PT100 embedded in motor | °C | 4-20 mA | 5 sec | Thermal health feature | Trending up without load change = insulation fail
12 | Bearing Temperature (DE/NDE) | PT100 on bearing housing | °C | 4-20 mA | 5 sec | Bearing wear indicator | ΔTemp >10°C from baseline = lubrication fail
13 | Run Hours (total lifetime) | Software Counter | hrs | Modbus RTU | 1 min | Remaining useful life estimate | Combined with starts count for lifecycle model
14 | Start Count | Software Counter | Count | Modbus RTU | Per event | Starting stress accumulation | Each start = stress cycle on windings/capacitor
15 | Starter Type / Transition Status | DI on Starter Panel | Enum | Digital Input | Per event | Soft start quality feature | Star-delta transition shock vs soft starter
16 | VFD Output Frequency (if fitted) | VFD Register | Hz | Modbus RTU | 1 sec | Speed-health correlation | Efficiency map vs current speed setpoint
17 | Fault / Trip History | Relay + SCADA log | Enum | Digital Input | Per event | Failure mode labelling | Ground truth for supervised failure model

## 04 Water Quality Risk Model
04 WATER QUALITY RISK MODEL
WHAT: Calculates risk score, propagation zone and probable cause hours before a compliance breach. |  |  |  |  | WHY IT MATTERS: Proactive safety — stops contamination reaching citizens before regulators are informed.
Category: Quality |  | Total Parameters: 12
# | Parameter Name | Source Asset | Unit | Sensor / Transmitter | Protocol | Sampling Rate | AI Feature Role | Notes / Alert Condition
1 | Residual Chlorine | Chlorine Analyser (online) | mg/L | 4-20 mA / Modbus | 5 min | Primary quality indicator | < 0.2 mg/L triggers compliance alert
2 | Turbidity | Turbidity Sensor (online) | NTU | 4-20 mA / Modbus | 5 min | Contamination ingress signal | Sudden spike = mains intrusion or soil entry
3 | pH Level | pH Probe (online) | pH | 4-20 mA / Modbus | 5 min | Chemical balance indicator | pH < 6.5 or > 9.5 = treatment failure
4 | Conductivity / TDS | Conductivity Sensor | µS/cm | 4-20 mA / Modbus | 5 min | Salinity / contamination proxy | Rising TDS = aquifer contamination risk
5 | Temperature (water) | Temperature Sensor (inline) | °C | 4-20 mA | 5 min | Bacterial growth risk feature | >25°C promotes Legionella growth
6 | Pressure (network zone) | Pressure Transmitter | bar | 4-20 mA / HART | 1 min | Intrusion risk — negative pressure | Transient negative pressure = contamination ingress
7 | Flow Rate (zone) | Electromagnetic Flow Meter | m³/h | 4-20 mA / Modbus RTU | 1 min | Stagnation / retention time estimate | Low flow = long retention = chlorine decay
8 | Water Level (UGR / Service Res.) | Ultrasonic Level Transmitter | m | 4-20 mA / Modbus | 5 min | Reservoir retention time | High level + low demand = stagnation risk
9 | Valve Status (zone isolation) | Limit Switch / Actuator | Open/Closed | Modbus RTU / DI | 1 min | Network topology for propagation model | Closed valves define contamination boundary
10 | Pump Running Status | DI on Starter | On/Off | Digital Input | 1 sec | Treatment dosing flow context | Pumping without dosing = residual collapse
11 | Chlorine Dose Rate | Dosing Pump / Flow Controller | L/h | 4-20 mA / Modbus | 5 min | Treatment adequacy feature | Dose vs flow ratio = effective residual
12 | Bulk Water Meter Reading | Bulk Water Meter | m³ | Pulse / Modbus RTU | 15 min | Consumption-decay correlation | Low consumption zones = high decay risk

## 05 Demand Forecasting Engin
05 DEMAND FORECASTING ENGINE
WHAT: Projects demand, tank levels and supply requirements 6–24 hours ahead per distribution zone. |  |  |  |  | WHY IT MATTERS: Enables proactive supply scheduling — eliminates reactive shortfalls and supply inequity.
Category: Supply |  | Total Parameters: 12
# | Parameter Name | Source Asset | Unit | Sensor / Transmitter | Protocol | Sampling Rate | AI Feature Role | Notes / Alert Condition
1 | Bulk Water Meter (zone inlet) | Bulk Water Meter | m³ | Pulse / Modbus RTU | 15 min | Historical demand pattern (primary) | Zone-level 24h rolling consumption profile
2 | Flow Rate (instantaneous) | Electromagnetic Flow Meter | m³/h | 4-20 mA / Modbus RTU | 1 min | Real-time demand signal | Actual vs forecast deviation trigger
3 | Water Level — UGR | Ultrasonic Level Transmitter | m | 4-20 mA / Modbus | 5 min | Storage buffer state | Falling level = supply insufficient for demand
4 | Water Level — Overhead Tank (OHT) | Ultrasonic Level Transmitter | m | 4-20 mA / Modbus | 5 min | Distribution buffer state | OHT low = scheduled pump required
5 | Pump Run Status (all pumps) | DI on Starter Panel | On/Off | Digital Input | 1 sec | Current supply rate context | Which pumps are contributing to supply
6 | Pump Flow Rate (per pump) | Electromagnetic Flow Meter | m³/h | 4-20 mA / Modbus RTU | 1 min | Per-pump supply contribution | Used to allocate demand across pump schedule
7 | VFD Frequency (if fitted) | VFD Register | Hz | Modbus RTU | 1 sec | Variable speed flow control | Speed setpoint vs zone pressure/demand
8 | Pressure (zone) | Pressure Transmitter | bar | 4-20 mA / HART | 1 min | Demand-pressure relationship | Pressure-dependent demand modelling
9 | Discharge Sluice Valve Status | Actuator / Limit Switch | Open/Closed | Modbus RTU / DI | 1 min | Network availability state | Valve closed = zone isolated from supply
10 | ATS / Changeover Switch Status | DI on ATS Panel | Mains/DG | Digital Input | 1 sec | Power availability context | DG mode = limited pump capacity
11 | Energy Consumption (kWh) | Energy Meter on LT Panel | kWh | Modbus RTU | 15 min | Supply cost per m³ optimisation | Schedule shifts to off-peak tariff windows
12 | Run Hours (per pump) | Software Counter | hrs | Modbus RTU | 1 min | Available pump capacity | Exclude pumps near maintenance threshold

## 06 Root Cause Assistant
06 ROOT CAUSE ASSISTANT
WHAT: Delivers plain-English incident explanations with ranked recommended actions in real time. |  |  |  |  | WHY IT MATTERS: Cuts fault diagnosis from hours to minutes — junior staff operate at expert engineer level.
Category: Ops |  | Total Parameters: 14
# | Parameter Name | Source Asset | Unit | Sensor / Transmitter | Protocol | Sampling Rate | AI Feature Role | Notes / Alert Condition
1 | Fault / Trip Status (all assets) | Relay Output / DI on all panels | Enum | Digital Input | Per event | Event trigger — root cause context | Trip event initiates root cause analysis
2 | Motor Current (all 3 phases) | CT Sensor | A | Modbus RTU | 1 sec | Phase fault pattern recognition | Single-phase loss, overload signature
3 | Voltage (R-Y-B phases) | PT / Energy Meter | V | Modbus RTU | 1 sec | Supply quality at time of fault | Voltage sag correlates with network fault
4 | Flow Rate at time of fault | Electromagnetic Flow Meter | m³/h | 4-20 mA / Modbus RTU | 1 sec | Hydraulic state context | No flow + running pump = valve closed or burst
5 | Pressure at time of fault | Pressure Transmitter | bar | 4-20 mA / HART | 1 sec | System state at fault moment | Pressure spike = waterhammer event
6 | Vibration at time of fault | Vibration Sensor | mm/s | 4-20 mA / Modbus | 1 sec | Mechanical fault signature | High vibration before trip = bearing/impeller
7 | Bearing Temperature | PT100 | °C | 4-20 mA | 5 sec | Thermal root cause evidence | Temperature pre-fault trend analysis
8 | Winding Temperature | PT100 in Motor | °C | 4-20 mA | 5 sec | Thermal overload root cause | Insulation breakdown pattern
9 | Starter Status at fault | DI on Starter | Enum | Digital Input | Per event | Starting mode context | Star-delta transition fail vs run fault
10 | Valve Positions at fault | Limit Switch / Actuator | Open/Closed | Modbus RTU / DI | Per event | Hydraulic topology at fault | Closed valve = root cause of no-flow trip
11 | UGR/Sump Level at fault | Ultrasonic Level Transmitter | m | 4-20 mA / Modbus | 5 sec | Supply-side fault context | Empty sump = dry run trip root cause
12 | Power Supply Status (ATS/DG) | DI on ATS | Mains/DG | Digital Input | Per event | Power root cause (grid vs DG fault) | Mains failure = ATS cause, not pump cause
13 | Historical fault log | SCADA / PLC event log | Log | Modbus TCP / SCADA DB | Continuous | Fault pattern matching | Similar past events ranked by similarity
14 | Alarm sequence (pre-fault) | SCADA alarm log | Log | SCADA DB | Continuous | Causal chain reconstruction | Alarm cascade sequence identifies root cause

## 07 NRW Attribution Engine
07 NRW ATTRIBUTION ENGINE
WHAT: Separates real losses from apparent losses — attributing variance to leaks, meter errors or theft. |  |  |  |  | WHY IT MATTERS: Tells management where to act — not just how much is being lost. Investment becomes targeted.
Category: Revenue |  | Total Parameters: 12
# | Parameter Name | Source Asset | Unit | Sensor / Transmitter | Protocol | Sampling Rate | AI Feature Role | Notes / Alert Condition
1 | Bulk Water Meter — Zone Inlet | Bulk Water Meter (inlet) | m³ | Pulse / Modbus RTU | 15 min | System input volume | Primary NRW calculation input
2 | Bulk Water Meter — Zone Outlet | Bulk Water Meter (outlet) | m³ | Pulse / Modbus RTU | 15 min | Zone boundary metering | Inlet - Outlet = zone losses
3 | Electromagnetic Flow Meter | Inline Flow Meter (DMA) | m³/h | 4-20 mA / Modbus RTU | 1 min | Real-time loss rate | Flow imbalance per DMA = pinpoints loss zone
4 | Night Minimum Flow (02-04h) | Aggregated from flow meters | m³/h | SCADA aggregation | 1 min | Background real loss index | NMF - legitimate night use = real leakage
5 | Pressure (zone average) | Multiple Pressure Transmitters | bar | 4-20 mA / HART | 15 min | Pressure-leakage exponent (N1 model) | Higher pressure = exponentially more leakage
6 | Consumer Meter Reading | AMR / Smart Meter | m³ | AMR / Pulse / GPRS | 1 hr | Authorised consumption baseline | Billed volume vs metered zone input
7 | Discharge Sluice Valve Position | Actuator Position Feedback | % | Modbus RTU / 4-20 mA | 5 min | Zone topology — loss boundary | Valve state defines NRW accounting boundary
8 | NRV Check Valve Status | Limit Switch | Open/Closed | Digital Input | 5 min | Reverse flow / backflow losses | Faulty NRV = backflow = apparent losses
9 | Pump Run Hours | Software Counter | hrs | Modbus RTU | 1 min | Supply volume cross-check | Hours × rated flow vs bulk meter = meter error
10 | Water Level — UGR | Ultrasonic Level Transmitter | m | 4-20 mA / Modbus | 5 min | Storage volume change | ΔLevel × area = supply volume correction
11 | Flushing Valve Status | Limit Switch | Open/Closed | Digital Input | Per event | Operational loss tracking | Flushing volume subtracted from NRW calc
12 | Solenoid Valve Status | DI | On/Off | Digital Input | Per event | Controlled use vs unaccounted loss | Identify unauthorised operation events

## 08 Energy Optimisation AI
08 ENERGY OPTIMISATION AI
WHAT: Recommends optimal pump schedules using off-peak tariff windows, demand curves and efficiency. |  |  |  |  | WHY IT MATTERS: Reduces pumping cost automatically — the largest variable OpEx — without manual intervention.
Category: Cost |  | Total Parameters: 15
# | Parameter Name | Source Asset | Unit | Sensor / Transmitter | Protocol | Sampling Rate | AI Feature Role | Notes / Alert Condition
1 | Active Power (kW) per pump | Energy Meter on LT Panel | kW | Modbus RTU | 1 min | Real-time energy cost signal | Cost per m³ = kW / flow rate (specific energy)
2 | Reactive Power (kVAR) | Energy Meter / APFC Panel | kVAR | Modbus RTU | 5 min | Power factor penalty cost | Low PF = kVAR charge from utility
3 | Energy Consumption (kWh) | Energy Meter | kWh | Modbus RTU | 15 min | Tariff window billing tracking | Off-peak vs peak kWh comparison
4 | Power Factor | APFC Panel / Energy Meter | PF | Modbus RTU | 5 min | Capacitor bank switching optimisation | Target PF > 0.95 to avoid utility penalty
5 | Flow Rate (per pump) | Electromagnetic Flow Meter | m³/h | 4-20 mA / Modbus RTU | 1 min | Specific energy (kWh/m³) calculation | Pump efficiency curve operating point
6 | Discharge Pressure | Pressure Transmitter | bar | 4-20 mA / HART | 1 min | System resistance curve point | Throttling losses = wasted energy
7 | Suction Pressure | Pressure Transmitter | bar | 4-20 mA / HART | 1 min | Net head calculation | Differential head = energy per m³ pumped
8 | VFD Frequency / Speed Setpoint | VFD Register | Hz | Modbus RTU | 1 sec | Speed optimisation signal | Affinity laws: speed² ∝ power → huge savings
9 | UGR Water Level | Ultrasonic Level Transmitter | m | 4-20 mA / Modbus | 5 min | Storage buffer for off-peak scheduling | Fill UGR at off-peak; coast through peak
10 | OHT / Tank Level | Ultrasonic Level Transmitter | m | 4-20 mA / Modbus | 5 min | Demand buffer state | High tank = delay next pump start
11 | Pump Run Hours (lifetime) | Software Counter | hrs | Modbus RTU | 1 min | Schedule balances wear across pumps | Rotate duty/standby to equalise hours
12 | ATS Status (Mains vs DG) | DI on ATS | Enum | Digital Input | 1 sec | Tariff mode — DG running cost context | DG fuel cost >> mains; avoid DG pumping
13 | Motor Current (all phases) | CT Sensor | A | Modbus RTU | 1 sec | Motor efficiency point tracking | Current vs speed vs flow = efficiency map
14 | Capacitor Bank Step Status | DI on APFC Panel | On/Off | Digital Input | 1 min | Reactive compensation adequacy | Optimise APFC switching to hold PF target
15 | Pump Start/Stop Schedule | SCADA / PLC setpoint | Schedule | Modbus TCP | Per command | Schedule optimisation output | AI output drives pump start/stop commands

## Sensor Master List
Sensor / Transmitter Type | Protocol | Unit | Used In AI Models | Count of Uses
Modbus RTU | 1 min / 1 sec / 15 min / 5 min / 5 sec / Per event | A / Count / Hz / PF / V / hrs / kVAR / kW / kWh | Anomaly Detection, Demand Forecasting Engine, Energy Optimisation AI, Leak / Burst Classifier, NRW Attribution Engine, Pump Health Model, Root Cause Assistant | 24
4-20 mA / Modbus | 1 min / 1 sec / 5 min / 5 sec | % / L/h / NTU / m / mg/L / mm/s / pH / µS/cm | Anomaly Detection, Demand Forecasting Engine, Energy Optimisation AI, Leak / Burst Classifier, NRW Attribution Engine, Pump Health Model, Root Cause Assistant, Water Quality Risk Model | 20
Digital Input | 1 min / 1 sec / 5 min / 5 sec / Per event | Enum / Mains/DG / On/Off / Open/Closed | Anomaly Detection, Demand Forecasting Engine, Energy Optimisation AI, Leak / Burst Classifier, NRW Attribution Engine, Pump Health Model, Root Cause Assistant, Water Quality Risk Model | 16
4-20 mA / HART | 1 min / 1 sec / 15 min | bar | Anomaly Detection, Demand Forecasting Engine, Energy Optimisation AI, Leak / Burst Classifier, NRW Attribution Engine, Pump Health Model, Root Cause Assistant, Water Quality Risk Model | 13
4-20 mA / Modbus RTU | 1 min / 1 sec | m³/h | Anomaly Detection, Demand Forecasting Engine, Energy Optimisation AI, Leak / Burst Classifier, NRW Attribution Engine, Pump Health Model, Root Cause Assistant, Water Quality Risk Model | 10
4-20 mA | 5 min / 5 sec | °C | Anomaly Detection, Pump Health Model, Root Cause Assistant, Water Quality Risk Model | 6
Pulse / Modbus RTU | 1 min / 15 min | m³ | Anomaly Detection, Demand Forecasting Engine, Leak / Burst Classifier, NRW Attribution Engine, Water Quality Risk Model | 6
Modbus RTU / DI | 1 min / 5 sec / Per event | Open/Closed | Demand Forecasting Engine, Leak / Burst Classifier, Root Cause Assistant, Water Quality Risk Model | 4
Modbus RTU (aggregated) | 1 min | m³/h | Leak / Burst Classifier | 1
Modbus TCP / SCADA DB | Continuous | Log | Root Cause Assistant | 1
SCADA DB | Continuous | Log | Root Cause Assistant | 1
SCADA aggregation | 1 min | m³/h | NRW Attribution Engine | 1
AMR / Pulse / GPRS | 1 hr | m³ | NRW Attribution Engine | 1
Modbus RTU / 4-20 mA | 5 min | % | NRW Attribution Engine | 1
Modbus TCP | Per command | Schedule | Energy Optimisation AI | 1